## Slide 1: CASE STUDY: ANOMALY DETECTION With Industrial PC-based Energy Measurement Framework
PRESENTED BY
Bhagyashree Popat Zaware
Eduardo Guandulain Juárez
Muhammad Munam Uddin Farooqui
Nnamdi Ogbonnaya Odii
Yuganshu Whadhwa
Rohit Arunachalam Gopinath

## Slide 2: Agenda
Overview
Data Acquisition
Communication
Algorithm
Results

## Slide 3: Overview
Problem Statement
  The objective is to develop and implement an anomaly detection solution to identify
  real-time failures in power systems.
Solution Concept
  BECKHOFF Industrial PC and TwinCAT 3 to monitor and analyze power signals.
  Algorithm to detect anomalies.
Expected Benefits
  Improved efficiency, reduced downtime, corrective maintenance.

## Slide 4: Experimental Setup
24V DC Power Supply
Beckhoff’s IPC hosting TwinCAT 3
Beckhoff’s I/O terminals
  EK 1100
  EL 3783
220Ω resistive load on a breadboard
Digilent Analog Discovery 2
Computer monitor
Waveform signal generator

## Slide 5: Data Acquisition
WaveForms Generation Software
Data acquisition using TwinCAT 3

## Slide 6: Power Failure
Value from AnalogDiscovery2
= 4V - 0v - 4v
Voltage at the terminals
= 1,65V - 0v - 1,65V
Time
= 15s - 90s - 15s
Voltage Magnitude < 0.1 pu for 3s - 1min

## Slide 7: Voltage Sag
Value from AnalogDiscovery2
= 4 V - 3.2V - 4v
Voltage at the terminals
= 1.65V - 1.32V - 1.65V
Time
= 45s - 30s - 45s
Voltage Magnitude: 0.1 - 0.9pu for 3s - 1min

## Slide 8: Voltage Swell
Value from AnalogDiscovery2
= 4 V - 4.8v - 4v
Voltage at the terminals
= 1.65V - 1.98V - 1.65V
Time
= 45s - 30s - 45s
Voltage Magnitude
1.1 - 1.2 pu for 3s - 1min

## Slide 9: Undervoltage
Value from AnalogDiscovery2
= 4 V - 3.2v - 4v
Voltage at the terminals
= 1.65V - 1.32V - 1.65V
Time
= 25s - 70s - 25s
Voltage Magnitude
0.8 - 0.9 pu for > 1min

## Slide 10: Overvoltage
Value from AnalogDiscovery2
= 4 V - 4.8v - 4v
Voltage at the terminals
= 1.65V - 1.98V - 1.65V
Time
= 25s - 70s - 25s
Voltage Magnitude:
1.1 - 1.2 pu for > 1min

## Slide 11: Electrical Noise
Value from AnalogDiscovery2
= 4 V - 4v / 50Hz with 10kHz - 4v
Value at the terminals
= 1.65 V - 1.65v / 50Hz with 10kHz - 4v
Time
= 45s - 30s - 45s

## Slide 12: Frequency Variation
Value from AnalogDiscovery2
= 4V / 50Hz - 4V / 60Hz - 4V / 50Hz
Voltage at the terminals
= 1.65 / 50Hz - 1.65V / 60Hz - 1.65V / 50Hz
Time
= Same for > 10 s

## Slide 13
TwinCAT 3 Setup

## Slide 14: Communication
TWINCAT 3
OVERSAMPLING MODULE
Reads Data every 50µs and stores in
an array of 100 values
PLC fetches data every 5ms.
Array of 100 values
PLC
PYTHON
(Anomaly Detection)
ANOMALY DETECTION ALGORITHM
For Anomoly detection we need 10 cycles of data(4000 data samples) according to IEEE standard.
PYTHON
(Data Acquisition)
Communication
PyADS
Read and write
Notification based

## Slide 15: Communiction
Approaches:
  ADS- PyADS Read/Write
  Buffer Creation
  ADS Notification

## Slide 16: ADS Communication
Adapted from https://infosys.beckhoff.com/english.php?content=../content/1033/cx8190_hw/5091854987.html&id=

## Slide 17: PyADS Read/ Write

## Slide 18: Buffer With PyADS
FB_MemRingBuffer: FIFO Buffer
Implementation Unsuccessful
FB_MemStackBuffer: LIFO Buffer
Not Useful in our Case
Buffer through loop and different PLC Tasks

## Slide 19: Buffer Creation

## Slide 20: Buffer Results

## Slide 21
ADS Notification
Communication via notifications instead of individual
read requests
PUSH instead of PULL
Unsuccessful implementation

## Slide 22: Comparison and direction for future
ADS read/write
ADS notifications
Data Buffer
Data loss ??
Time issue ??
TwinCAT 3 expertise ??

## Slide 23: Overview Of The Algorithm
V, I Signals (Noisy)
V, I Signals (Smooth)
10 Cycle Window for 50 Hz
As per IEEE Standard 1564-2014
Transient Behavior Variations
Interruptions
Voltage Sag
Voltage Swell
Frequency Behavior Variations
Prime Harmonic Variation
THD Calculation

## Slide 24: Calculation Of Rms Voltage
Why?
To analyze the transient behavior of the system (Identify: sags, swells, and interruptions based on predefined thresholds)
The value of the rms voltage is measured over one cycle and refreshed each half cycle.
          N – Number of samples per cycle
          – Sampled voltage waveform
          k – 1,2,3, etc.
As per IEEE Standard 1564-2014

## Slide 25: Detection Of Transient Anomalies
S. No | Categories | Typical Duration (Cycles) | Typical Duration (Seconds) | Typical Voltage Magnitude
1 | Short Duration RMS |  |  | 
1.1 | Instantaneous |  |  | 
1.1.1 | Sag | 0.5–30 cycles | 0.01 - 0.6 Seconds | 0.1–0.9 pu
1.1.2 | Swell | 0.5–30 cycles | 0.01 - 0.6 Seconds | >1.1 pu
1.2 | Momentary |  |  | 
1.2.1 | Interruption | 0.5 cycles – 3s | 0.01 - 3 Seconds | < 0.1 pu
1.2.2 | Sag | 30 cycles – 3 s | 0.6 - 3 Seconds | 0.1–0.9 pu
1.2.3 | Swell | 30 cycles – 3 s | 0.6 - 3 Seconds | >1.1 pu
1.3 | Temporary |  |  | 
1.3.1 | Interruption |  | >3 Seconds – 1 Minute | < 0.1 pu
1.3.2 | Sag |  | >3 Seconds – 1 Minute | 0.1–0.9 pu
1.3.3 | Swell |  | >3 Seconds – 1 Minute | >1.1 pu
2 | Long Duration RMS |  |  | 
2.1 | Power Failure |  | > 1 Minute | <0.1 pu
2.2 | Under - Voltage |  | > 1 Minute | 0.1–0.9 pu
2.3 | Over - Voltage |  | > 1 Minute | >1.1 pu
As per IEEE Standard 1159-2019

## Slide 26: Calculation Of Total Harmonic Distortion (THD)
Why?
To quantify the distortion in a power system's voltage waveform by quantitatively analyzing the effect of present Harmonics in the signal.
          N – Total Number of Harmonic present in the signal
          – Magnitude of kth Harmonic Component
          – Magnitude of Prime Harmonic Frequency
          k – 1,2,3, etc.
As per IEEE Standard 519-2014

## Slide 27: Processing Of Raw Data
Current & Voltage data received from TwinCAT in the form of CSV file.
Name - Time Stamp (LDAP)
I_L1real - Current
U_L1real - Voltage

## Slide 28: Converting LDAP Timestamps
Lightweight Directory Access Protocol (LDAP) timestamp.
  Represent the number of 100-nanosecond intervals since January 1, 1601 (UTC).
Why ?
  Provides high precision - crucial for accurately recording events in time-sensitive applications.
Raw data consist of LDAP Timestamps which is converted to human readable format. (YYYY-MM-DD HH:MM:SS)
Why ?
  Data analysis and Visualization.

## Slide 29: Modifying Time Stamp
Raw data from TwinCAT is cleaned by
dropping null values, and other
columns are removed.
Timestamp column is renamed
from Name > Time

## Slide 30: Lowpass Filtering
Why?
Removes high-frequency noise from the signal, making it easier to detect anomalies.
Before Filtering
After Filtering
10 Cycle Window for 50 Hz
As per IEEE Standard 1564-2014

## Slide 31: Results
Successful detection of RMS Variation Anomalies:

## Slide 32: Results
Successful detection of THD Variation Anomalies:

## Slide 33: REFERENCES
https://pyads.readthedocs.io/en/latest/index.html
https://www.beckhoff.com/en-en/products/automation/twincat/tc1xxx-twincat-3-base/tc1000.html
https://infosys.beckhoff.com/english.php?content=../content/1033/tcplclib_tc2_utilities/35010187.html&id=
https://download.beckhoff.com/download/document/automation/twincat3/TF6701_TC3_IoT_Communication_MQTT_EN.pdf
https://infosys.beckhoff.com/index.php?content=../content/1031/tcadsnetref/7312578699.html&id=
IEE Recommended Practice for Monitoring Electric Power Quality, The Institute of Electrical and Electronics Engineers, Inc. 345 East 47th Street, New York, NY 10017-2394, USA. Copyright © 1995 by the Institute of Electrical and Electronics Engineers, Inc.